## 主系統 Take-Off
主系統編號（含 Take-Off 編號） | 系統別 | 系統名稱 | 管線樣式 | 接點尺寸 | 接點形式 | 最大流量（LPM） | 樓層
SB_A01_SiH4_01-01 | Special Gas | SiH4 | jacketed | 1/4" | VCR | 5 | L30
SB_A01_SiH4_01-02 | Special Gas | SiH4 | jacketed | 1/4" | VCR | 5 | L30
SB_A01_HF_01-01 | Special Gas | HF-49% | jacketed | 1/4" | VCR | 2 | L20
SB_A01_NH3_01-01 | Special Gas | NH3 | heated | 1/4" | VCR | 3 | L30

## Bulk Gas
設備名稱 | 接點編號 | 系統名稱 | 接點尺寸 | 接點形式 | 最大流量（LPM） | 最小壓力（kgf/cm²） | 最大壓力（kgf/cm²） | 樓層
Mainframe | HPPIK01-1-05 | CDA | 1/2" | Sw | 300 | 8 | 7 | L30
Mainframe | HPPIK01-1-06 | CDA | 1/2" | Sw | 300 | 8 | 7 | L30
Mainframe | HPPIK01-1-07 | CDA | 1/2" | Sw | 300 | 8 | 7 | L30
Mainframe | HPPIK01-1-08 | CDA | 1/2" | Sw | 300 | 8 | 7 | L30
Mainframe | HPPIK01-1-09 | CDA | 1/2" | Sw | 300 | 8 | 7 | L30
Chemical Box | HPPIK01-6-10 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
Chemical Box | HPPIK01-6-11 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
Chemical Box | HPPIK01-6-12 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
Chemical Box | HPPIK01-6-13 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
Chemical Box | HPPIK01-6-14 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
Chemical Box | HPPIK01-6-15 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
Chemical Box | HPPIK01-6-16 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
Chemical Box | HPPIK01-6-17 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
Chemical Box | HPPIK01-6-18 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
Chemical Box | HPPIK01-6-19 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
THC | HPPIK01-4-20 | CDA | 3/8" | Sw | 120 | 8 | 7 | L20
CDA-GUN | HPPIK01-7-21 | CDA | 1/4" | Qu |  | 8 | 7 | L30
Mainframe | HPPIK01-1-22 | PN2 | 1/2" | Sw | 150 | 7 | 5 | L30
Mainframe | HPPIK01-1-23 | PN2 | 1/2" | Sw | 150 | 7 | 5 | L30
Mainframe | HPPIK01-1-24 | PN2 | 1/2" | Sw | 150 | 7 | 5 | L30
Mainframe | HPPIK01-1-25 | PN2 | 1/2" | Sw | 150 | 7 | 5 | L30
Mainframe | HPPIK01-1-26 | PN2 | 1/2" | Sw | 150 | 7 | 5 | L30
Mainframe | HPPIK01-1-27 | PN2 | 1/2" | Sw | 150 | 7 | 5 | L30
Mainframe | HPPIK01-1-28 | PN2 | 1/2" | Sw | 200 | 7 | 5 | L30
Mainframe | HPPIK01-1-29 | PN2 | 1/2" | Sw | 150 | 7 | 5 | L30
Mainframe | HPPIK01-1-30 | PN2 | 1/2" | Sw | 150 | 7 | 5 | L30
Chemical Box | HPPIK01-6-31 | PN2 | 3/8" | Sw | 100 | 7 | 5 | L30
Chemical Box | HPPIK01-6-32 | PN2 | 3/8" | Sw | 100 | 7 | 5 | L30
Chemical Box | HPPIK01-6-33 | PN2 | 3/8" | Sw | 100 | 7 | 5 | L30
Mainframe | HEPOA01-10-21 | CDA | 3/8" | Sw | 66 | 5.6 |  | L30
Mainframe | HEPOA01-10-22 | CDA | 3/8" | Sw | 66 | 5.6 |  | L30
Dry Pump LL | HEPOA01-20-23 | GN2 | 1/4" | Qum | 10 | 2.5 | 7 | L10
Dry PumpBuffer | HEPOA01-21-24 | GN2 | 1/4" | Qum | 10 | 2.5 | 7 | L10
Dry Pump Chamber | HEPOA01-17-25 | GN2 | 1/4" | Qum | 44 | 2.5 | 7 | L10
Dry Pump Chamber | HEPOA01-18-26 | GN2 | 1/4" | Qum | 44 | 2.5 | 7 | L10
Dry Pump Chamber | HEPOA01-19-27 | GN2 | 1/4" | Qum | 44 | 2.5 | 7 | L10
Local Scrubber A | HEPOA01-15-28 | GN2 | 3/8" | Sw | 300 | 5.1 | 6.1 | L10
Local Scrubber A | HEPOA01-15-29 | CDA | 1/2" | Sw | 210 | 5.1 | 6.1 | L10
三合一地板 | HEPOA01-24-30 | CDA | 1/4" | Qu |  |  |  | L30
GAS Panel | HEPOA01-4-31 | PO2 | 1/4" | VCR | 0.2 | 2 |  | L30
GAS Panel | HEPOA01-4-32 | PO2 | 1/4" | VCR | 0.2 | 2 |  | L30
GAS Panel | HEPOA01-4-33 | PO2 | 1/4" | VCR | 0.2 | 2 |  | L30
GAS Panel | HEPOA01-4-34 | PAr | 1/4" | VCR | 0.2 | 2 |  | L30
GAS Panel | HEPOA01-4-35 | PAr | 1/4" | VCR | 0.2 | 2 |  | L30
GAS Panel | HEPOA01-4-36 | PAr | 1/4" | VCR | 0.2 | 2 |  | L30
GAS Panel | HEPOA01-4-37 | PHe | 1/4" | VCR | 0.5 | 2 |  | L30
GAS Panel | HEPOA01-4-38 | PHe | 1/4" | VCR | 0.5 | 2 |  | L30
GAS Panel | HEPOA01-4-39 | PHe | 1/4" | VCR | 0.5 | 2 |  | L30
GAS Panel | HEPOA01-4-40 | PN2 | 1/4" | VCR | 1 | 2 |  | L30
Mainframe | HEPOA01-10-41 | PN2 | 1/4" | VCR | 40 | 2 |  | L30
Mainframe | HEPOA01-10-42 | PN2 | 1/4" | VCR | 100 | 2 |  | L30
Mainframe | HEPOA01-10-43 | PHe | 1/4" | VCR | 0.015 | 2 |  | L30

## Chemical
設備名稱 | 接點編號 | 系統名稱 | 接點尺寸 | 接點形式 | 最大流量（LPM） | 最小壓力（kgf/cm²） | 最大壓力（kgf/cm²） | 樓層
Mainframe | SGMK01-1-01 | SiH4 | 1/4" | VCR | 5 | 1 | 5 | L30
Mainframe | SGMK01-1-02 | SiH4 | 1/4" | VCR | 5 | 1 | 5 | L30
Mainframe | SGMK01-1-03 | HF-49% | 1/4" | VCR | 2 | 1 | 3 | L20
Mainframe | SGMK01-1-04 | NH3 | 1/4" | VCR | 3 | 1 | 4 | L30

## PCW
設備名稱 | 接點編號 | 系統名稱 | 接點尺寸 | 接點形式 | 最大流量（LPM） | 最小壓力（kgf/cm²） | 最大壓力（kgf/cm²） | 樓層
Mainframe | DIFFA01-1-01 | PCWS | 1" | Fl | 120 | 3.5 | 3 | L20
Mainframe | DIFFA01-1-02 | PCWS | 1" | Fl | 80 | 3.5 | 3 | L20
Tube Cooling | DIFFA01-2-03 | PCWS | 1/2" | Sw | 30 | 3 | 2.5 | L20
Mainframe | DIFFA01-1-04 | PCWR | 1" | Fl | 120 | 3.5 | 3 | L20
Mainframe | DIFFA01-1-05 | PCWR | 1" | Fl | 80 | 3.5 | 3 | L20
Tube Cooling | DIFFA01-2-06 | PCWR | 1/2" | Sw | 30 | 3 | 2.5 | L20
Mainframe | DIFFA02-1-07 | PCWS | 1" | Fl | 150 | 3.5 | 3 | L20
Mainframe | DIFFA02-1-08 | PCWS | 1" | Fl | 75 | 3.5 | 3 | L20
Mainframe | DIFFA02-1-09 | PCWR | 1" | Fl | 150 | 3.5 | 3 | L20
Mainframe | DIFFA02-1-10 | PCWR | 1" | Fl | 75 | 3.5 | 3 | L20
Mainframe | CVDA01-1-01 | PCWS | 3/4" | Sw | 60 | 3 | 2.5 | L10
Dry Pump | CVDA01-3-02 | PCWS | 1/2" | Sw | 25 | 3 | 2.5 | L10
Chiller | CVDA01-4-03 | PCWS | 1/2" | Sw | 35 | 3 | 2.5 | L10
Mainframe | CVDA01-1-04 | PCWR | 3/4" | Sw | 60 | 3 | 2.5 | L10
Dry Pump | CVDA01-3-05 | PCWR | 1/2" | Sw | 25 | 3 | 2.5 | L10
Chiller | CVDA01-4-06 | PCWR | 1/2" | Sw | 35 | 3 | 2.5 | L10
Mainframe | CVDA02-1-07 | PCWS | 3/4" | Sw | 75 | 3 | 2.5 | L10
Dry Pump | CVDA02-3-08 | PCWS | 1/2" | Sw | 30 | 3 | 2.5 | L10
Mainframe | CVDA02-1-09 | PCWR | 3/4" | Sw | 75 | 3 | 2.5 | L10
Dry Pump | CVDA02-3-10 | PCWR | 1/2" | Sw | 30 | 3 | 2.5 | L10

## Special Gas
設備名稱 | 接點編號 | 系統名稱 | 接點尺寸 | 接點形式 | 最大流量（LPM） | 最小壓力（kgf/cm²） | 最大壓力（kgf/cm²） | 樓層
Mainframe | SGMK01-1-01 | SiH4 | 1/4" | VCR | 5 | 1 | 5 | L30
Mainframe | SGMK01-1-02 | SiH4 | 1/4" | VCR | 5 | 1 | 5 | L30
Mainframe | SGMK01-1-03 | HF-49% | 1/4" | VCR | 2 | 1 | 3 | L20
Mainframe | SGMK01-1-04 | NH3 | 1/4" | VCR | 3 | 1 | 4 | L30

## City Water
設備名稱 | 接點編號 | 系統名稱 | 接點尺寸 | 接點形式 | 最大流量（LPM） | 最小壓力（kgf/cm²） | 最大壓力（kgf/cm²） | 樓層
Local Scrubber | CVDA01-5-01 | LSW | 3/4" | Sw | 60 | 3 | 2.5 | L10
Local Scrubber | CVDA01-5-02 | SCRW | 3/4" | Sw | 60 | 3 | 2.5 | L10
Local Scrubber | CVDA02-5-01 | LSW | 1/2" | Sw | 30 | 3 | 2.5 | L10
Local Scrubber | CVDA02-5-02 | SCRW | 1/2" | Sw | 30 | 3 | 2.5 | L10

## Process Vacuum
設備名稱 | 接點編號 | 系統名稱 | 接點尺寸 | 接點形式 | 最大流量（LPM） | 最小壓力（kgf/cm²） | 最大壓力（kgf/cm²） | 樓層

## Pumping Line
設備名稱 | 接點編號 | 系統名稱 | 接點尺寸 | 接點形式 | 最大流量（LPM） | 最小壓力（kgf/cm²） | 最大壓力（kgf/cm²） | 樓層

## Drain
設備名稱 | 接點編號 | 系統名稱 | 接點尺寸 | 接點形式 | 最大流量（LPM） | 最小壓力（kgf/cm²） | 最大壓力（kgf/cm²） | 樓層

## 人工派點
主系統編號（含 Take-Off 編號） | Take-Off 樓層 | 接點編號 | 派點名稱（選填）
SB_A01_SiH4_01-01 | L30 | SGMK01-1-01 | SGMK01-SiH4-1
SB_A01_SiH4_01-02 | L30 | SGMK01-1-02 | SGMK01-SiH4-2
SB_A01_HF_01-01 | L20 | SGMK01-1-03 | SGMK01-HF-1
SB_A01_NH3_01-01 | L30 | SGMK01-1-04 | SGMK01-NH3-1

## 系統別清單 (hidden)
BOE
Cyclopentanone
EBR
H2O2-30%
H2SO4-96%
HCl-37%
HF-0.5%
HF-49%
HNO3
IPA
M1
M2
NH4OH-27%
PGMEA
TMAH-2.38%
HCl-36%
TEOS

## 管線樣式
# | 系統別 | 系統名稱 | 管線樣式（內管） | 管線樣式（外管） | 管線樣式（加熱） | ACI 色碼 | 說明 | 備註
1 | Bulk Gas | IC-B | SUS304 BA. |  |  |  | Interconnect
2 | Bulk Gas | BA | SUS304 BA. |  |  |  | Breathing air
3 | Bulk Gas | CDA | SUS304 BA. |  |  |  | Clean dry air
4 | Bulk Gas | PCDA | SUS304 BA. |  |  |  | CDA high pressure
5 | Bulk Gas | HCDA | SUS304 BA.
6 | Bulk Gas | XCDA | SUS316L EP.
7 | Bulk Gas | CDA-Gun | SUS304 BA. |  |  |  | CDA for Gun
8 | Bulk Gas | GN2 | SUS304 BA. |  |  |  | N2, Nitrogen standard
9 | Bulk Gas | LN2 | SUS304 BA. |  |  |  | L-N2, Liquid Nitrogen
10 | Bulk Gas | PN2 | SUS316L EP. |  |  |  | N2, Nitrogen purified
11 | Bulk Gas | N2-Gun | SUS304 BA. |  |  |  | N2 Nitrogen for Gun
12 | Bulk Gas | He-Gun | SUS316L EP. |  |  |  | He, purified for Gun
13 | Bulk Gas | UO2 | SUS304 AP.
14 | Bulk Gas | UN2 | SUS304 AP.
15 | Bulk Gas | UCA | SUS304 AP. |  |  |  | CDA, Scrubber
16 | Bulk Gas | SA | SUS304 AP.
17 | Bulk Gas | O2S | SUS304 AP. |  |  |  | O2 for scrubber
18 | Special Gas | IC-S | SUS316L EP. |  |  |  | Interconnect
19 | Special Gas | PAr | SUS316L EP. |  |  |  | Ar, Argon purified
20 | Special Gas | PHe | SUS316L EP. |  |  |  | He, Helium purified
21 | Special Gas | PO2 | SUS316L EP. |  |  |  | O2, Oxygen purified
22 | Special Gas | 0.1%PH3/N2 | SUS316L EP. |  |  |  | 0.1% Phosphine in Nitrogen
23 | Special Gas | 0.5%PH3/N2 | SUS316L EP. |  |  |  | 0.5% Phosphine in Nitrogen
24 | Special Gas | 0.5%O2/He | SUS316L EP. |  |  |  | 0.5%Oxygen in Helium
25 | Special Gas | 0.95%F2/1.25%Kr/Ne | SUS316L EP. |  |  |  | (OLD DO NOT USE) 0.95% Fluor 1.25% Krypton in Neon
26 | Special Gas | 0.95%F2/1.25%Kr/Ne | SUS316L EP. |  |  |  | 0.95% Fluor 1.25% Krypton in Neon
27 | Special Gas | 0.95%F2/3.5%Ar/Ne | SUS316L EP. |  |  |  | 0.95% Fluor 3.5% Argon in Neon
28 | Special Gas | 1%B2H6/H2 | SUS316L EP. |  |  |  | 1% Diborane in Hydrogen
29 | Special Gas | 1%F2/1.2%Kr/Ne | SUS316L EP. |  |  |  | 1% Fluor 1.2% Krypton in Neon
30 | Special Gas | 1%F2/3.6%Kr/Ne | SUS316L EP. |  |  |  | 1% Fluor 3.6% Krypton in Neon
31 | Special Gas | 1%GeH4/H2 | SUS316L EP. |  |  |  | 1% Germane in Hydrogen
32 | Special Gas | 1%O2/Ar | SUS316L EP. |  |  |  | 1% Oxygen in Argon
33 | Special Gas | 1%PH3/He | SUS316L EP. |  |  |  | 1% Phosphine in Helium
34 | Special Gas | 1%PH3/N2 | SUS316L EP. |  |  |  | 1% Phosphine in Nitrogen
35 | Special Gas | 1.2%He/N2 | SUS316L EP. |  |  |  | 1.2% Helium in Nitrogen
36 | Special Gas | 1.2%He/O2 | SUS316L EP. |  |  |  | 1.2% Helium in Oxygen
37 | Special Gas | 1.2%Kr/Ne | SUS316L EP. |  |  |  | 1.2% Krypton in Neon
38 | Special Gas | 1.25%Kr/Ne | SUS316L EP. |  |  |  | 1.25% Krypton in Neon
39 | Special Gas | 10%CH4/Ar | SUS316L EP. |  |  |  | 10% Methane in Argon
40 | Special Gas | 10%GeH4/H2 | SUS316L EP. |  |  |  | 10% Germane in Hydrogen
41 | Special Gas | 15%B2H6/H2 | SUS316L EP. |  |  |  | 15% Diborane in Hydrogen
42 | Special Gas | 15%B2H6/N2 | SUS316L EP. |  |  |  | 15% Diborane in Nitrogen
43 | Special Gas | 2.7%C2H4/He | SUS316L EP. |  |  |  | 2.7% Ethylene in Helium
44 | Special Gas | 20%F2/N2 | SUS316L EP. |  |  |  | 20% Flour in Nitrogen
45 | Special Gas | 3.5%Ar/10ppmXe/Ne | SUS316L EP. |  |  |  | 3.5% Argon 10ppmXenon in Neon
46 | Special Gas | 3.6%Ar/10ppmXe/Ne | SUS316L EP. |  |  |  | 3.6% Argon 10ppmXenon in Neon
47 | Special Gas | 30%O2/He | SUS316L EP. |  |  |  | 30% Oxygen in Helium
48 | Special Gas | 4%H2/N2 | SUS316L EP. |  |  |  | 4% Hydrogen in Nitrogen
49 | Special Gas | 5%B2H6/N2 | SUS316L EP. |  |  |  | 5% Diborane in Nitrogen
50 | Special Gas | 5%BCl3/He | SUS316L EP. |  |  |  | 5% Boron Trichloride in Helium
51 | Special Gas | 5%H2/He | SUS316L EP. |  |  |  | 5%Hydrogen in Helium
52 | Special Gas | 5%PH3/N2 | SUS316L EP. |  |  |  | 5% Phosphine in Nitrogen
53 | Special Gas | 99%Kr | SUS316L EP. |  |  |  | 99% Krypton
54 | Special Gas | AsH3 | SUS316L EP.
55 | Special Gas | B2H6 | SUS316L EP. |  |  |  | Diborane
56 | Special Gas | BCl3 | SUS316L EP. |  |  |  | Boron Trichloride
57 | Special Gas | BF3 | SUS316L EP.
58 | Special Gas | C2H2 | SUS316L EP. |  |  |  | Acethylen
59 | Special Gas | C2H4 | SUS316L EP. |  |  |  | Ethylene
60 | Special Gas | C3F8 | SUS316L EP. |  |  |  | Octafluorpropane
61 | Special Gas | C3H6 | SUS316L EP. |  |  |  | Propene
62 | Special Gas | C4F6 | SUS316L EP. |  |  |  | Hexafluorbutadiene
63 | Special Gas | C4F8 | SUS316L EP. |  |  |  | Octaflurocyclobutane
64 | Special Gas | CF4 | SUS316L EP. |  |  |  | Tetrafluormethane
65 | Special Gas | CH2F2 | SUS316L EP. |  |  |  | Difluormethane
66 | Special Gas | CH3F | SUS316L EP. |  | Insulation |  | Methylfluoride
67 | Special Gas | CH4 | SUS316L EP. |  | Insulation |  | Methane
68 | Special Gas | CHF3 | SUS316L EP. |  | Insulation |  | Trifluormethane
69 | Special Gas | Cl2 | SUS316L EP. |  | Insulation |  | Chlorine
70 | Special Gas | ClF3 | SUS316L EP. |  | Heating Jacket |  | Chlorine trifluoride
71 | Special Gas | CO | SUS316L EP. |  | Heating Jacket |  | Carbon Monoxide
72 | Special Gas | CO2 | SUS316L EP. |  | Heating Jacket |  | Carbon Dioxide
73 | Special Gas | COS | SUS316L EP. |  | Heating Jacket |  | Carbonylsulfid
74 | Special Gas | GC02 | SUS316L EP. | SUS304 AP. |  |  | SPECIAL CO2 for Litho
75 | Special Gas | GeF4 | SUS316L EP. | SUS304 AP.
76 | Special Gas | GeH4 | SUS316L EP. | SUS304 AP. |  |  | Germane
77 | Special Gas | H9NSi3 | SUS316L EP. | SUS304 AP.
78 | Special Gas | HBr | SUS316L EP. | SUS304 AP. |  |  | Hydrogen bromide
79 | Special Gas | HCl-Gas | SUS316L EP. | SUS304 AP. |  |  | Hydrogen chloride
80 | Special Gas | HF | SUS316L EP. | SUS304 AP. |  |  | OLD, DO NOT USE (Hydroflouric)
81 | Special Gas | HF-D | SUS316L EP. | SUS304 AP. |  |  | HF GAS for Diffusion
82 | Special Gas | HF-E | SUS316L EP. | SUS304 AP. |  |  | HF GAS for ETCH
83 | Special Gas | HF-Gas | SUS316L EP. | SUS304 AP. |  |  | Hydroflouric
84 | Special Gas | IC-PS | SUS316L EP. | SUS304 AP. |  |  | Interconnect
85 | Special Gas | Kr | SUS316L EP. | SUS304 AP. |  |  | Krypton
86 | Special Gas | N2O | SUS316L EP. | SUS304 AP. |  |  | Nitrous oxide
87 | Special Gas | NF3 | SUS316L EP. | SUS304 AP. |  |  | Nitrogene Trifluoride
88 | Special Gas | NG | SUS304 AP. |  |  |  | Natural gas
89 | Special Gas | NH3 | SUS316L EP. | SUS304 AP. |  |  | Ammonia
90 | Special Gas | NO | SUS316L EP. | SUS304 AP. |  |  | Nitrogene monoxide
91 | Special Gas | O3 | SUS316L EP. | SUS304 AP. |  |  | OLD, DO NOT USE (Ozone)
92 | Special Gas | P-H2 | SUS316L EP. | SUS304 AP. |  |  | Hydrogen Purified
93 | Special Gas | PH3 | SUS316L EP. | SUS304 AP. |  |  | Phosphine
94 | Special Gas | Precursor | SUS316L EP. | SUS304 AP.
95 | Special Gas | SF6 | SUS316L EP. | SUS304 AP. |  |  | Sulfur hexafluoride
96 | Special Gas | Si(CH3)3H | SUS316L EP. | SUS304 AP.
97 | Special Gas | Si2H6 | SUS316L EP. | SUS304 AP. |  |  | Disilane HP
98 | Special Gas | SiCl4 | SUS316L EP. | SUS304 AP. |  |  | Siliciumtetrachlorid
99 | Special Gas | SiF4 | SUS316L EP. | SUS304 AP. |  |  | TetrafluoroSilane
100 | Special Gas | SiH2Cl2 | SUS316L EP. | SUS304 AP. |  |  | Dichlorsilane (DCS)
101 | Special Gas | SiH4 | SUS316L EP. | SUS304 AP. | Insulation |  | Silane
102 | Special Gas | SO2 | SUS316L EP. | SUS304 AP. | Insulation |  | Sulfurdioxide
103 | Special Gas | t.b.d. - PS | SUS316L EP. | SUS304 AP. | Insulation |  | K4-PS to be defined
104 | Special Gas | TEB-GAS | SUS316L EP. | SUS304 AP. | Insulation
105 | Special Gas | TEOS-GAS | SUS316L EP. | SUS304 AP. | Heating Jacket |  | OLD, DO NOT USE (Tetraethyortosilicate Gas)
106 | Special Gas | TEPO-GAS | SUS316L EP. | SUS304 AP. | Heating Jacket
107 | Special Gas | TiCl4 | SUS316L EP. | SUS304 AP. | Heating Jacket
108 | Special Gas | WF6 | SUS316L EP. | SUS304 AP. | Heating Jacket |  | Tungsten Hexafluoride
109 | Chemical | IC-C | PFA | CPVC |  |  | Interconnect
110 | Chemical | Anji H6S | PFA | CPVC |  |  | Anji H6S
111 | Chemical | Anji T800 | PFA | CPVC |  |  | Anji T800
112 | Chemical | Anji T800S | PFA | CPVC |  |  | Anji T800S
113 | Chemical | Anji U3061 | PFA | CPVC |  |  | Anji U3061
114 | Chemical | AP2100F | PFA | CPVC |  |  | AP2100F
115 | Chemical | Cabot 7300A | PFA | CPVC |  |  | Cabot 7300A
116 | Chemical | Cabot 7300B | PFA | CPVC |  |  | Cabot 7300B
117 | Chemical | Cabot 7573B | PFA | CPVC |  |  | Cabot 7573B
118 | Chemical | CuSO4 | PFA | CPVC |  |  | CuSO4
119 | Chemical | CuSO4-an | PFA | CPVC |  |  | OLD, DO NOT USE (CuSO4 anolyze)
120 | Chemical | CuSO4-cat | PFA | CPVC |  |  | OLD, DO NOT USE (CuSO4 catholyte)
121 | Chemical | DEV 2.37% | PFA | CPVC |  |  | DEV TMAH 2.37%
122 | Chemical | DEV 25% | PFA | CPVC |  |  | DEV 25%
123 | Chemical | Dow 1501 | PFA | CPVC |  |  | Dow 1501
124 | Chemical | DP001 | PFA | CPVC |  |  | FN-DP001
125 | Chemical | DP001T | PFA | CPVC |  |  | OLD, DO NOT USE (FN-DP001T)
126 | Chemical | EBR | PFA | CPVC |  |  | OLD, DO NOT USE (EBR Litho Solvent PGMEA)
127 | Chemical | EBR-1 | PFA | CPVC |  |  | EBR-1 Litho Solvent PGMEA
128 | Chemical | EKC5670 | PFA | CPVC |  |  | EKC5670
129 | Chemical | Fujimi 6120 | PFA | CPVC |  |  | Fujimi 6120
130 | Chemical | Fujimi 6125N | PFA | CPVC |  |  | Fujimi 6125N
131 | Chemical | H2O2-30% | PFA | CPVC |  |  | OLD, DO NOT USE (Hydrogenperoxid 30%)
132 | Chemical | H2O2-31% | PFA | CPVC |  |  | Hydrogenperoxid 31%
133 | Chemical | H2SO4-96% | PFA | CPVC |  |  | Sulfuric acid 96%
134 | Chemical | H3PO4-80% | PFA | CPVC |  |  | OLD, DO NOT USE (Phosphoric acid)
135 | Chemical | H3PO4-85% | PFA | CPVC |  |  | Phosphoric acid 85%
136 | Chemical | H4 | PFA | CPVC |  |  | H4
137 | Chemical | HCl-36% | PFA | CPVC |  |  | Hydrochloric acid
138 | Chemical | HF-100:1 | PFA | CPVC |  |  | Hydrofluoric acid 100:1
139 | Chemical | HF-49% | PFA | CPVC |  |  | Hydrofluoric acid 49%
140 | Chemical | Hitachi HS0220 | PFA | CPVC |  |  | Hitachi HS0220
141 | Chemical | HMDS | PFA | CPVC |  |  | Hexamethyldisilazan (C6H19NSi2)
142 | Chemical | HNO3-69% | PFA | CPVC |  |  | OLD, DO NOT USE (Nitric acid 69%)
143 | Chemical | HNO3-70% | PFA | CPVC |  |  | Nitric acid 70%
144 | Chemical | HSN | PFA | CPVC |  |  | HSN
145 | Chemical | ICS8000 | PFA | CPVC |  |  | ICS8000
146 | Chemical | IPA | PFA | CPVC |  |  | Isopropanol
147 | Chemical | NaOH | PFA | CPVC |  |  | Sodiumhydroxide
148 | Chemical | NH4OH 2% | PFA | CPVC |  |  | Ammoniumhydroxide 2%
149 | Chemical | NH4OH-28% | PFA | CPVC |  |  | OLD, DO NOT USE (Ammoniumhydroxide 28%)
150 | Chemical | NH4OH-29% | PFA | CPVC |  |  | Ammoniumhydroxide 29%
151 | Chemical | OK73 | SUS316L EP. |  |  |  | OK73
152 | Chemical | RP002 | SUS316L EP. |  |  |  | FN-RP002
153 | Chemical | SPC-402A | SUS316L EP. | SUS304 AP. |  |  | AZSPC-402
154 | Chemical | ST250 | SUS316L EP. | SUS304 AP. |  |  | Stripper 250
155 | Chemical | STI2100 | PFA | SUS304 AP. |  |  | STI2100
156 | Chemical | t.b.d. - PC | PFA | SUS304 AP. |  |  | PC to be defined
157 | Chemical | T800 | PFA | SUS304 AP. |  |  | T800
158 | Chemical | T8005 | PFA | SUS304 AP. |  |  | T8005
159 | Chemical | YXL-100 | PFA | SUS304 AP. |  |  | YXL-100
160 | Pure Cooling Water | IC-W | SUS304 |  |  |  | Interconnect
161 | Pure Cooling Water | PCWR | SUS304 |  |  |  | PCW Return
162 | Pure Cooling Water | PCWS | SUS304 |  |  |  | PCW Supply
163 | Ultra Pure Water | IC-U | PVDF |  |  |  | Interconnect
164 | Ultra Pure Water | CDIR | PP. |  |  |  | Cold DI Return
165 | Ultra Pure Water | CDIS | PVDF |  |  |  | Cold DI Supply
166 | Ultra Pure Water | HDIR | PP. |  |  |  | Hot DI Return
167 | Ultra Pure Water | HDIS | PVDF |  |  |  | Hot DI Supply
168 | Ultra Pure Water | UPWR | PP. |  |  |  | Ultra Pure Water Return
169 | Ultra Pure Water | UPWS | PVDF |  |  |  | Ultra Pure Water Supply
170 | City Water |  | PP. |  |  |  | Interconnect
171 | City Water | LSW | PP. |  |  |  | Local Scrubber Water
172 | City Water | SCRW | PP. |  |  |  | Local Scrubber Water
173 | Exhaust | IC-X | PSP. |  |  |  | Interconnect
174 | Exhaust | CA | GS. |  |  |  | Clean Air Litho
175 | Exhaust | SEX | PSP. |  |  |  | Acid
176 | Exhaust | SEX(U) | PSP. |  |  |  | Acid Floor 3 UP
177 | Exhaust | AEX | PSP. |  |  |  | Ammonia
178 | Exhaust | AEX(U) | PSP. |  |  |  | Ammonia, Floor 3 UP
179 | Exhaust | EEX | PSP. |  |  |  | Air Return
180 | Exhaust | XAS | PSP. |  |  |  | With Arsenic
181 | Exhaust | XAS(U) | PSP. |  |  |  | With Arsenic, Floor 3 UP
182 | Exhaust | GEX | GS. |  |  |  | General
183 | Exhaust | GEX(U) | GS. |  |  |  | General Floor 3 UP
184 | Exhaust | VEX | PSP. |  |  |  | Solvent
185 | Exhaust | XPM | PSP. |  |  |  | Hoods
186 | Exhaust | Vent | SUS316L EP.
187 | Process Vacuum | IC-V | PVDF |  |  |  | Interconnect
188 | Process Vacuum | House Vacuum | PVDF |  |  |  | House Vacuum
189 | Process Vacuum | PV | PVDF |  |  |  | Process vac Equipment
190 | Process Vacuum | CV | PVDF
191 | Pumping Line | PHV | SUS304L |  |  |  | Foreline
192 | Pumping Line | SCR | SUS304L |  |  |  | Scrubber line
193 | Pumping Line | Vent | SUS316L EP.
194 | Drain | IC-D | PVDF |  |  |  | Interconnect
195 | Drain | D-ARC | PP 10. |  |  |  | ARC+HMDS
196 | Drain | D-CCu | PP 10. |  |  |  | Concentrated Copper Waste
197 | Drain | D-CH2SO4 | PP 10. |  |  |  | Sulfuric acid >70%
198 | Drain | D-CH3PO4 | PP 10. |  |  |  | Phosphoric acid >70%
199 | Drain | D-CHF | PP 10. |  |  |  | waste conc. HF>10%
200 | Drain | D-CMP Cu | PP 10. |  |  |  | CMP Copper Waste
201 | Drain | D-CMP Metal | PP 10. |  |  |  | CMP Metal waste
202 | Drain | D-CMP Oxide | PP 10. |  |  |  | CMP Oxide waste
203 | Drain | D-DCu | PP 10. |  |  |  | Dilute Copper Waste
204 | Drain | D-DH2SO4 | PP 10. |  |  |  | Sulfuric acid 50-70%
205 | Drain | D-DHF | PP 10. |  |  |  | waste dilute HF<2%
206 | Drain | D-DIR | PP 10. |  |  |  | DI Rinse
207 | Drain | D-DIR/O3 | PP 10. |  |  |  | O3 reclaim
208 | Drain | D-H2SO4-C | PP 10. |  |  |  | Sulfuric acid >50%
209 | Drain | D-HF/IPA | PP 10. |  |  |  | HF + IPA
210 | Drain | D-HNO3 | PP 16. |  |  |  | HNO3>1000ppm exclude HF
211 | Drain | D-IPA | PP 16. |  |  |  | IPA>5%
212 | Drain |  | PP 16. |  |  |  | IPA<5%
213 | Drain | D-LSR | PP 16. |  |  |  | Local Scrubber drain
214 | Drain | D-MA | PP 16. |  |  |  | High Concentration mixing acid
215 | Drain |  | PP 16. |  |  |  | High Concentration mixing acid,Dynamic drainage
216 | Drain | D-NF | PP 16. |  |  |  | NH4F>5%
217 | Drain | D-NH4OH | PP 16. |  |  |  | NH4OH>50ppm
218 | Drain | D-Org | PP 16. |  |  |  | Organic solvent drain
219 | Drain |  | PP 16. |  |  |  | Organic solvent drain,Dynamic drainage
220 | Drain | D-PIQ | PVDF |  |  |  | PIQ resist
221 | Drain | D-PR | PVDF |  |  |  | PR+HMDS
222 | Drain | D-SOD | PVDF |  |  |  | SOD Local Waste
223 | Drain | D-TMAH | PVDF |  |  |  | TMAH
224 | Drain | D-WWA | PVDF |  |  |  | Acid DL; Base DL; >3000µS/cm
225 | Drain | t.b.d. - PA | PVDF |  |  |  | PA to be defined

## 管徑
# | 系統別 | 最小管徑 | 最大管徑
1 | Bulk Gas | 1/4" | 1-1/2"
2 | Special Gas | 1/4" | 3/4"
3 | PCW | 1/4" | 2"
4 | Chemical | 1/4" | 3/4"
5 | City Water | 1/4" | 2"
6 | Process Vacuum | 1/4" | 1-1/2"
7 | Pumping Line | 2" | 18"
8 | Exhaust | 4" | 18"
9 | Power | 20A | 600A
10 | Ultra Pure Water | 1/4" | 2"
11 | Drain | 1/4" | 2"
12 | 其他 | 1/4" | 1/2"

## 填寫說明
import_excel.xlsx 填寫說明
▌ 整體使用流程
步驟 | 動作 | 說明
步驟 1 | 填寫機台設備接點 | Bulk Gas / Chemical / PCW / Special Gas / City Water / Process Vacuum / Pumping Line / Drain 八個 Sheet，每個接點填一行
步驟 2 | 填寫主系統 Take-Off | 列出所有供氣主幹線 Take-Off 接點，每個 Take-Off 填一行
步驟 3 | 填寫人工派點（選填） | 需手動指定 Take-Off ↔ 機台接點對應時才填；否則系統自動配對
步驟 4 | 上傳此 Excel 至 YAHO | 系統自動產生 AutoLISP TXT，透過 AutoCAD 匯出 P&ID DWG
▌ 各 Sheet 說明
Sheet 名稱 | 用途 | 必填 / 選填 | 填入對象
主系統 Take-Off | 供氣主幹線 Take-Off 接點清單 | 必填 | 每個 Take-Off 一行
Bulk Gas | Bulk Gas 系統（N2、CDA、GN2 等）機台設備接點 | 必填（依需求） | 每個接點一行
Chemical | 化學品（液體）系統機台設備接點 | 必填（依需求） | 每個接點一行
PCW | PCW 製程冷卻水系統機台設備接點 | 必填（依需求） | 每個接點一行
Special Gas | 特殊氣體系統機台設備接點 | 必填（依需求） | 每個接點一行
City Water | City Water 市水系統（LSW / SCRW 局部洗滌塔用水）機台設備接點 | 必填（依需求） | 每個接點一行
Process Vacuum | Process Vacuum 製程真空系統機台設備接點 | 必填（依需求） | 每個接點一行
Drain | Drain 排水系統機台設備接點 | 必填（依需求） | 每個接點一行
人工派點 | Take-Off ↔ 機台接點手動對應 | 選填 | 自動配對不足時補足
管線樣式 | 指定各系統別 ACI 管線顏色 | 選填 | 需自訂顏色時填入
管徑 | 各系統允許管徑範圍（系統參考用） | 選填 | 通常不需修改
▌ 主系統 Take-Off — 欄位說明
欄位名稱 | 說明 | 範例 | 必填
主系統編號（含 Take-Off 編號） | 唯一識別碼，建議格式：<廠區>_<機台代號>_<系統名>_<編號> | SB_A01_SiH4_01-01 | 必填
系統別 | 填入以下七種之一：Bulk Gas / Chemical / PCW / Special Gas / City Water / Process Vacuum / Drain（大小寫須一致） | Special Gas | 必填
系統名稱 | 氣體或流體名稱，須與對應機台設備 Sheet 中「系統名稱」完全一致 | SiH4、PCWS、CDA | 必填
管線樣式 | standard / jacketed / heated（見下方管線樣式對照表） | jacketed | 必填
接點尺寸 | 管件公稱尺寸（英制） | 1/4"、1/2"、1" | 必填
接點形式 | 連接形式代碼（見下方接點形式對照表） | VCR、Sw、Fl | 必填
最大流量（LPM） | Take-Off 側需求流量，升/分鐘，正整數 | 5、300 | 必填
樓層 | Take-Off 所在樓層代碼 | L10、L20、L30、LB1 | 必填
▌ 機台設備 Sheet（Bulk Gas / Chemical / PCW / Special Gas / City Water / Process Vacuum / Pumping Line / Drain）— 欄位說明
欄位名稱 | 說明 | 範例 | 必填
設備名稱 | 機台子系統或部件名稱，僅供標示（不影響產圖邏輯） | Mainframe、Chemical Box、Dry Pump | 必填
接點編號 | 唯一識別碼，格式：<機台 SBGL-ID>-<子系統編號>-<流水號> | HPPIK01-1-05 | 必填
系統名稱 | 氣體或流體名稱，須與主系統 Take-Off Sheet「系統名稱」完全一致 | CDA、PN2、PCWS | 必填
接點尺寸 | 管件公稱尺寸（英制） | 1/4"、1/2"、1" | 必填
接點形式 | 連接形式代碼（見下方對照表） | VCR、Sw、Fl、Qu、Qum | 必填
最大流量（LPM） | 升/分鐘；無規格時可空白（如快速接頭出口） | 300、可空白 | 必填（可空白）
最小壓力（kgf/cm²） | 機台端最低工作壓力，可空白 | 3.5、可空白 | 選填
最大壓力（kgf/cm²） | 機台端最高承受壓力，可空白 | 3、可空白 | 選填
樓層 | 接點所在樓層代碼 | L10、L20、L30 | 必填
▌ 人工派點 — 欄位說明
欄位名稱 | 說明 | 範例 | 必填
主系統編號（含 Take-Off 編號） | 對應主系統 Take-Off Sheet 的主系統編號，須完全一致 | SB_A01_SiH4_01-01 | 必填
Take-Off 樓層 | 此 Take-Off 所在樓層，須與主系統 Take-Off Sheet「樓層」欄位一致 | L20、L30 | 必填
接點編號 | 對應機台設備 Sheet 的「接點編號」，須完全一致 | SGMK01-1-01 | 必填
派點名稱（選填） | 自訂此配對的顯示名稱；留空則系統自動命名 | SGMK01-SiH4-1、可空白 | 選填
▌ 管線樣式對照
樣式名稱 | 外觀說明
standard | 單一實線。適用一般流體（如 N2、CO2）
double | 三條平行實線（双套管）。適用危險/毒性/腐蝕性流體，防洩漏設計
single + Insulation | 一條實線 + 兩條虛線（保溫棉）。適用需保溫以防結晶/液化的流體
single + heating | 一條實線 + 兩條虛線（加熱帶）。適用需加熱以防結晶/液化的流體
double + Insulation | 三條平行實線（双套管）+ 兩條虛線（保溫棉）。適用危險/毒性/腐蝕性且需要保溫的流體，防洩漏設計
double + heating | 三條平行實線（双套管）+ 兩條虛線（加熱帶）。適用危險/毒性/腐蝕性且需要保溫的流體，防洩漏設計
▌ 接點形式對照
代碼 | 全名 | 說明
VCR | VCR Metal Gasket Face Seal | 高純度金屬密封，半導體氣體標準接頭
Sw | Swagelok Compression Fitting | 卡套式壓縮接頭，一般工業氣體用
Fl | Flange | 法蘭接頭，大管徑或水路（PCW）常用
Qu | Quick Union / Quick Connect | 快速接頭（無性別），常用於 CDA 出口
Qum | Quick Union Male | 快速接頭（公頭），常用於幫浦 GN2 入口
Vm | VCR Male | VCR 公頭規格
Fc | Ferrule Compression | 管壓縮接頭
▌ 重要注意事項
• 各 Sheet 的「系統名稱」欄位必須完全一致（大小寫、特殊符號），系統才能正確配對 Take-Off 與機台接點。
• Chemical 與 Special Gas 是不同 Sheet，請勿將化學品（液體）與特殊氣體（高壓氣體）填入同一 Sheet。
• 接點編號在整份 Excel 中必須唯一，重複接點編號可能導致配對錯誤。
• 主系統 Take-Off 的「系統別」欄位僅接受：Bulk Gas、Chemical、PCW、Special Gas、City Water、Process Vacuum、Drain（大小寫須一致）。
• 管線樣式 Sheet 的 ACI 色碼填入 1–255 整數；空白或超出範圍的值系統自動忽略並自動指派顏色。
• 人工派點 Sheet 的「主系統編號」與「接點編號」須與對應 Sheet 完全一致，否則該配對將被忽略。
• Pumping Line 為「內聯（IC）」系統：接點彼此直接對連、不接 Take-Off，故無需在「主系統 Take-Off」或「人工派點」填寫 Pumping Line。
• 內聯（IC）命名規範：在機台設備「接點編號」後綴加 -ICxx（例 PUMPA-01-IC01）即為內聯點；相同 ICxx 的接點會互相連接（1 對 1 或 1 對多開 Tee）。
• ICxx 為跨系統通用：跨系統內連（如 Special Gas 連至 Pumping Line）以相同 ICxx 表示，圖面於管末以斷管符號標示「TO 對端設備 對端系統別」。
• 內聯編碼目前由人工填寫，請確保相連接點 ICxx 完全一致（含前導零，IC01 與 IC1 視為不同）。